| THE VILLAGE OF JAMESTOWN has prepared the following report to provide information to you, the consumer, on the quality of our drinking water. Included within this report is general health information, water quality test results, how to participate in decisions concerning your drinking water and water system contacts. In order to ensure that tap water is safe to drink, USEPA prescribes regulations which limit the amounts of certain contaminants in water provided by public water systems. FDA regulations establish limits for contaminants in bottled eater which must provide the same protection for public health. The Village of Jamestown receives its drinking water from the "south well field" located on the southern property line of 807 State Route 72, South, In 2025, as in all years, extensive testing is done to ensure our drinking water is safe. As you can see on the chart included in this report, no contaminants were found that reached the level of a violation as specified by the Ohio Environmental Protection Agency. The contaminants that are listed on the chart all consist of compounds which are formed as a by-product of drinking water chlorination. Chlorine is used in our water supply for two reasons. First, chlorine acts as an oxidant in the raw well water supply previous to filtration. The oxidizing characteristics of chlorine help to change iron in the well water from an insoluble state to a soluble state. This makes it more readily removable by sand filtration. Second, chlorine is used as a disinfectant. Chlorine is added at the water plant to eliminate any harmful bacteria present in the water before it is pumped into the distribution system. The presence of a residual chlorine in the water throughout the distribution also protects the water from bacteriological contamination during the time it remains within the system. ANTI-CORROSION CONTROL. This control program has been in place now for several years. Anti-corrosion control methods were put in place several years ago as required by the Ohio EPA. The goal of this program is to ensure that no unsafe level of lead or copper is found in our water supply. This program involves the addition of a blended polyphosphate to the drinking water. The phosphate will form a molecular thin film on the village water mains a well as household plumbing. This film will prohibit the water from contacting the surface of any pipe of plumbing fixture, thus reducing the leaching of lead or copper from those pipes or fixtures. The addition of this polyphosphate is monitored daily by plant staff and monthly by the Ohio EPA, based on independent laboratory analysis provided to them. The effectiveness of this program was verified in 2003 when the lead and copper testing showed no detectable levels of lead or copper in any of the homes tested. Testing was repeated in 2021. If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children. Lead in drinking water is primarily from materials and components associated with service lines and home plumbing. THE VILLAGE OF JAMESTOWN is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components. When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking. If you are concerned about lead in your water, you may wish to have your water tested. Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from Safe Drinking Water Hotline at http://www.epa.gov/safewater/lead. OHIO EPA DRINKING WATER SOURCE ASSESSMENT REPORT FINDINGS. Ohio EPA recently completed a study of Jamestown's source of drinking water, to identify potential contaminant sources and provide guidance on protecting the drinking water source. According to this study, the aquifer (water-rich zone) that supplies water to Jamestown has a moder-ate susceptibility to contamination. This determination is based on the following: - Presence of a moderately thick protective layer of clay overlying the aquifer. - No evidence to suggest that ground water has been impacted by any significant levels of chemical contaminants from human activities. Presence of significant potential contaminant sources in the protection area The susceptibility means that under currently existing conditions, the likelihood of the aquifer becoming contaminated is moderate. This likelihood can be minimized by implementing appropriate protective measures. More information about the source water assessment or what consumers can do to help protect the aquifer is available by calling the Water Dept. at 937-675-2951. WELL PROTECTION ZONE In 2016, the Village of Jamestown purchased seventeen acres of farm ground on the south side and immediately adjacent to the village well field. This purchase will ensure that no future chemical application or pollution activity of any kind will take place on this acreage. It will also provide the location for potential new well development should the need arise. | WHAT ARE SOURCES OF CONTAMINATION OF DRINKING WATER? The sources of drinking water both tap and bottled water include rivers, lakes, streams, ponds, reservoirs, springs and wells. As water travels over the surface of the land or through the ground, it dissolves naturally-occurring minerals and, in some cases, radioactive mate-rial, and can pick up substances resulting from the presence of animals or from human activity. Contaminants that may be present in source water include: (A) Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations and wild-life: (B)Inorganic contaminants, such as salts and metals, which can be naturally-occurring or result from urban storm water runoff, industrial or domestic wastewater discharges, oil and gas production, mining or farming: (C) Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban storm water runoff, and residential uses: (D) Organic chemical contaminants, including synthetic and volatile organic chemicals. which are by-products of industrial processes and petroleum production, and can also come from gas stations, urban storm water runoff, and septic systems: (E) Radioactive contaminants, which can be naturally-occurring or be the result of oil and gas production and mining activities. Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency's Safe Drinking Water Hotline (1-800-426-4791 WHO NEEDS TO TAKE SPECIAL PRECAUTIONS? Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly and infants can be particularly at risk from infection. These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are avail-able from the Safe Drinking Water Hotline. (I-800-426-4791) ABOUT YOUR DRINKING WATER. The EPA requires regular sampling to ensure drinking water safety. In any given year, the Village of Jamestown conducts sampling for asbestos, HAA5’S, TTHMS, nitrate, nitrite, bacteria, inorganic, radiological, synthetic organic, and volatile organic contaminants. Samples were collected for a total of 70 different contaminants, most of which were not detected in the Village of Jamestown water supply. The Ohio EP requires us to monitor for some contaminants less than once per year because the concentrations of these contaminants do not change frequently. HOW DO I PARTICIPATE IN DECISIONS CONCERNING MY DRINKING WATER? Public participation and comment are encouraged at regular meetings of the Village council which meets the first and third Mondays of every month at 7:00 p.m. at the Village of Jamestown Municipal Building, 84 Seaman Drive, Jamestown, OH 45335. Additional information is available from the Water Department: (937) 675-2951 BACKFLOW PROTECTION PROGRAM The Village of Jamestown has a backflow program which has been monitored by the village since 2000.This program includes the oversight responsibility for the annual testing of all backflow devices in the village. Every year notifications are sent out to the water customers who have backflow devices. These devices are located at facilities which pose the greatest potential for backflow contamination which could lead to pos-sible health risk to our customers. Backflow occurs when water which has been compromised by a harmful pollutant is allowed to flow back into the public system. This can occur when a pressure differential is experienced., either due to a decrease of pressure in the public system or an increase of pressure in the private system. When these circumstances occur, a properly maintained backflow device will prevent water from the private system from flowing back into the public system. For this reason, the Village of Jamestown requires all backflow devices to be tested annually by a certified backflow examiner. These test results are submitted to the Village Water Department and are kept on file by the village. For more information on this program, contact the Water Dept. at 937-675-5311 and ask about our CCR. OEPA Unconditional License The Village had in 2025 and continues to have an OEPA unconditional license to operate our water system. Water Hardness? The Jamestown water treatment plant does not "soften" the water. The water is considered "very hard" with Total Hardness near 400 mg/L (23 grains per gallon). |
| --- | --- |

Jamestown Ohio 2025 CCR Water Quality Report

TABLE OF CONTAMINANTS

| Contaminants (units) | MCLG | MCL | Level Found | Range of Detection | Violation? | Test Year | Typical Sources of Contaminants |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Disinfection By- Products Sampling |  |  |  |  |  |  |  |
| 'l'rihalomethanes Total (ppb) | NA | 80 ppb | 9.2 ppb | 8.0- 9.2 | NO | 2025 | By- product of drinking water chlorination |
| Haloacetic Acids HAA5’s (ppb) | NA | 60 ppb | 5.5 ppb | ND- 5.5 | NO | 2025 | By- product of drinking water chlorination |
| Total Chlorine Residual sampling with Routine Bacteria sampling |  |  |  |  |  |  |  |
| Total Chlorine (ppm) | MRDL= 4 | MRDLG= 4 | 1.6 ppm | 1.08- 1.65 | NO | 2025 | Water additive used to control microbes |
| Inorganic Contaminants |  |  |  |  |  |  |  |
| Nitrate (ppm) | 10 | 10 | .13 ppm | NA | NO | 2023 | Erosion of Natural Deposits Runoff from fertilizer use, leaching from septic tanks sewage |
| Flouride (ppm) | 4 | 4 | 0.95 ppm | NA | NO | 2023 | Erosion of natural deposits |
| Barium Total (ppm) | 2 | 2 | 0.48 ppm | NA | NO | 2023 | Erosion of natural deposits |
| Arsenic (ppb) | 0 | 0 | 1 | 1-1 | NO | 2023 | Erosion of Natural Deposits Runoff from orchards |
| Cyanide (ppb) | 0 | 0 | 1 | 1-1 | NO | 2023 | Discharge from steel/metal factories and from elastic and fertilizer factories |
| Lead & Copper |  |  |  |  |  |  |  |
| Lead (ppb) | 0 | 15 AL | 90th% 2.8 ppb | ND- 3.4 | NO | 2025 | Corrosion of household plumbing materials |
| Copper(ppm) | 1.3 | 1.3 AL | 90th% 0.39 ppm | 0.02- 1.66 | NO | 2025 | Corrosion of household plumbing materials |
| 1 Copper sample exceeded the Action Level (AL) with a result of 1.66 ppm. 0 Lead samples exceeded the Action Level of 15 ppb. |  |  |  |  |  |  |  |

Definitions: MQLQ.; Maximum Contaminant Level Goal, or the level of a contaminant in drinking water below which there is no known or expected risk to health. MCLGs allow for a margin of safety. Maximum Contaminant Level, or the highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology. Action Level (AL) or the concentration of a contaminant which, when exceeded, triggers treatment or other requirements which a water system must follow. TT or Treatment Technique, or a required process intended to reduce the level of a contaminant in drinking water. MRDL: Maximum Residual Disinfectant, the highest level of a disinfectant allowed in drinking water. There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants. MRDLG: Maximum Residual Disinfectant Level Goal, the level of a drinking water disinfectant below which there is no known or expected risk to health. MRDLG do not reflect the benefits of the use of disinfectants to control microbial contamination. Abbreviations: •PPB: Parts per billion or micrograms per liter (a part per billion corresponds to one second in 31.7 years). •PPM: Parts per million or milligrams per liter(mg/L). •NA: not applicable. •NCFL: million fibers per liter. used to measure asbestos concentration. •ND: Not detectable at testing limits. •pCu/1: picocuries per liter Updates: In 2023 the MCL for Arsenic was 10 ppb, not O ppb. The MCL and MCLG for Cyanide should be 200 ppb, not O ppb. There was 1 Lead sample over action level @39.2 ppb. There was 1 Copper sample over action level @2.38 ppb. Revisions to the 2023 CCR included: A: The sourc3es of contaminations were missing in the table for nitrate, arsenic, and cyanide. B: The MCL for arsenic should be 10 ppb, not 0 ppb. C: The MCL and MCLG for cyanide should be 200 ppb, not 0 ppb. B: The statements regarding the number of samples found over the action level for lead and copper were missing in the report. Per the Lead and Copper Rules, Public Water Systems were required to develop and maintain a Service Line Inventory. A service line is the underground pipe that supplies your home or building with water. To view the Service Line Inventory, which lists the material type(s) for your location, you can visit our website jamestownohio.us or 84 Seaman Dr. Jamestown, Ohio 45335.

Tier 3 OHIO EPA Public Notice of Violation: The Village failed to certify notification to certain persons served by known or unknown or potential service lines containing lead. We were required to report a copy of the notice and materials sent to certain persons served by known or potential service lines containing lead to the State. Our system failed to demonstrate to the State that it delivered annual notifications and information to affected customers with lead, galvanized requiring replacement, or lead status unknown service lines as required by July 1, 2025. Although failure to comply with the reporting requirement does not create a risk to public health, we are required to inform you of this violation and provide additional information including what we did to correct the situation. WHAT SHOULD I DO? – There is nothing you need to do at this time. You do not need to boil your water or take other actions. Remember, boiling water does not remove lead from water. WHAT IS BEING DONE? – While we did not certify and notify the State as quickly as we should have, we provided the required notifications to certain persons served, as well as the missing information to the State on 9-26-2025. We are no longer in violation. For more information, please contact the Village Administrator, Brian Payton, at 937-675-2951 or send mail to P.O. Box 148, Jamestown, Ohio 45335. This notice is sent by the Jamestown Village PWS, PWS ID#OH2901712.

Published February 1, 2026